Customer Name:

CRM#:

Report Date:

Prepared by:

Approved by:

DER PQ

Benchmark/Compliance Report

# Introduction

The purpose of this report is to present a summary and supporting data to confirm the DER facility meets FortisAlberta DER-02/PQ-SPEC-01 compliance requirements when connecting to the FortisAlberta distribution system.

All texts in bold are for customer to fill in.

# Customer Description

Customer Name (Site ID, CRM#) at Location (LSD) in the area of Feeder is a DER customer with generation type Type of Generation and a maximum power output of Maximum allowed generation (MW) with power factor of Power Factor.

## Monitored Devices and Installations

The power quality monitor equipment for the purpose of power quality benchmark report shall be installed at the PCC and conforming to IEC 61000-4-30 Class A measurement standards.

The monitoring device shall be installed and take the measurement on the primary side (25kV). It is recommended that the customer provide a single line diagram indicating the location of monitoring in their facility.

Note: Either one of the following periods needs to be specified depending on the type of report (Benchmark or Compliance).

7 days of Benchmark monitoring period (Before generation): From Year-Month-Date to Year-Month-Date.

7 days of Compliance monitoring period (After Commissioning with normal generation): From Year-Month-Date to Year-Month-Date.

[Insert facility SLD indicating location of monitoring]

# Data Analysis and Graphs

## VRMS

Voltage RMS Graph

[Insert Voltage RMS Graph here]

Note: Vrms 95% weekly value should meet CSA C235 nomal operating conditions.

Based on rms voltage graph/data, the average voltage statistical data shows the following:

| 5th percentile |  |
| --- | --- |
| Average |  |
| 95th percentile |  |

## IRMS

Current RMS Graph

[Insert Current RMS Graph here]

## Voltage Unbalance

Voltage Unbalance Graph

[Insert Voltage Unbalance Graph here]

Note: Voltage unbalance (based on sequence components) should not exceed the limit of 3%.

## Voltage THD and Individual Voltage Harmonics Summary

The voltage harmonics are represented as a percentage (%) of the fundamental (60Hz) voltage for each phase accordingly.

Note: Compliant column is required for the compliance report but not required for benchmark report.

| V Harmonic | Average (%) | Maximum (%) | CP 95 (%) | Compliant (Yes/No) |
| --- | --- | --- | --- | --- |
| V THD A |  |  |  |  |
| V THD B |  |  |  |  |
| V THD C |  |  |  |  |
| V H2 A |  |  |  |  |
| V H2 B |  |  |  |  |
| V H2 C |  |  |  |  |
| V H3 A |  |  |  |  |
| V H3 B |  |  |  |  |
| V H3 C |  |  |  |  |
| V H4 A |  |  |  |  |
| V H4 B |  |  |  |  |
| V H4 C |  |  |  |  |
| V H5 A |  |  |  |  |
| V H5 B |  |  |  |  |
| V H5 C |  |  |  |  |
| V H6 A |  |  |  |  |
| V H6 B |  |  |  |  |
| V H6 C |  |  |  |  |
| V H7 A |  |  |  |  |
| V H7 B |  |  |  |  |
| V H7 C |  |  |  |  |
| V H8 A |  |  |  |  |
| V H8 B |  |  |  |  |
| V H8 C |  |  |  |  |
| V H9 A |  |  |  |  |
| V H9 B |  |  |  |  |
| V H9 C |  |  |  |  |
| V H10 A |  |  |  |  |
| V H10 B |  |  |  |  |
| V H10 C |  |  |  |  |
| V H11 A |  |  |  |  |
| V H11 B |  |  |  |  |
| V H11 C |  |  |  |  |
| V H12 A |  |  |  |  |
| V H12 B |  |  |  |  |
| V H12 C |  |  |  |  |
| V H13 A |  |  |  |  |
| V H13 B |  |  |  |  |
| V H13 C |  |  |  |  |
| V H14 A |  |  |  |  |
| V H14 B |  |  |  |  |
| V H14 C |  |  |  |  |
| V H15 A |  |  |  |  |
| V H15 B |  |  |  |  |
| V H15 C |  |  |  |  |
| V H16 A |  |  |  |  |
| V H16 B |  |  |  |  |
| V H16 C |  |  |  |  |
| V H17 A |  |  |  |  |
| V H17 B |  |  |  |  |
| V H17 C |  |  |  |  |
| V H18 A |  |  |  |  |
| V H18 B |  |  |  |  |
| V H18 C |  |  |  |  |
| V H19 A |  |  |  |  |
| V H19 B |  |  |  |  |
| V H19 C |  |  |  |  |
| V H20 A |  |  |  |  |
| V H20 B |  |  |  |  |
| V H20 C |  |  |  |  |
| V H21 A |  |  |  |  |
| V H21 B |  |  |  |  |
| V H21 C |  |  |  |  |
| V H22 A |  |  |  |  |
| V H22 B |  |  |  |  |
| V H22 C |  |  |  |  |
| V H23 A |  |  |  |  |
| V H23 B |  |  |  |  |
| V H23 C |  |  |  |  |
| V H24 A |  |  |  |  |
| V H24 B |  |  |  |  |
| V H24 C |  |  |  |  |
| V H25 A |  |  |  |  |
| V H25 B |  |  |  |  |
| V H25 C |  |  |  |  |
| V H26 A |  |  |  |  |
| V H26 B |  |  |  |  |
| V H26 C |  |  |  |  |
| V H27 A |  |  |  |  |
| V H27 B |  |  |  |  |
| V H27 C |  |  |  |  |
| V H28 A |  |  |  |  |
| V H28 B |  |  |  |  |
| V H28 C |  |  |  |  |
| V H29 A |  |  |  |  |
| V H29 B |  |  |  |  |
| V H29 C |  |  |  |  |
| V H30 A |  |  |  |  |
| V H30 B |  |  |  |  |
| V H30 C |  |  |  |  |
| V H31 A |  |  |  |  |
| V H31 B |  |  |  |  |
| V H31 C |  |  |  |  |
| V H32 A |  |  |  |  |
| V H32 B |  |  |  |  |
| V H32 C |  |  |  |  |
| V H33 A |  |  |  |  |
| V H33 B |  |  |  |  |
| V H33 C |  |  |  |  |
| V H34 A |  |  |  |  |
| V H34 B |  |  |  |  |
| V H34 C |  |  |  |  |
| V H35 A |  |  |  |  |
| V H35 B |  |  |  |  |
| V H35 C |  |  |  |  |
| V H36 A |  |  |  |  |
| V H36 B |  |  |  |  |
| V H36 C |  |  |  |  |
| V H37 A |  |  |  |  |
| V H37 B |  |  |  |  |
| V H37 C |  |  |  |  |
| V H38 A |  |  |  |  |
| V H38 B |  |  |  |  |
| V H38 C |  |  |  |  |
| V H39 A |  |  |  |  |
| V H39 B |  |  |  |  |
| V H39 C |  |  |  |  |
| V H40 A |  |  |  |  |
| V H40 B |  |  |  |  |
| V H40 C |  |  |  |  |
| V H41 A |  |  |  |  |
| V H41 B |  |  |  |  |
| V H41 C |  |  |  |  |
| V H42 A |  |  |  |  |
| V H42 B |  |  |  |  |
| V H42 C |  |  |  |  |
| V H43 A |  |  |  |  |
| V H43 B |  |  |  |  |
| V H43 C |  |  |  |  |
| V H44 A |  |  |  |  |
| V H44 B |  |  |  |  |
| V H44 C |  |  |  |  |
| V H45 A |  |  |  |  |
| V H45 B |  |  |  |  |
| V H45 C |  |  |  |  |
| V H46 A |  |  |  |  |
| V H46 B |  |  |  |  |
| V H46 C |  |  |  |  |
| V H47 A |  |  |  |  |
| V H47 B |  |  |  |  |
| V H47 C |  |  |  |  |
| V H48 A |  |  |  |  |
| V H48 B |  |  |  |  |
| V H48 C |  |  |  |  |
| V H49 A |  |  |  |  |
| V H49 B |  |  |  |  |
| V H49 C |  |  |  |  |
| V H50 A |  |  |  |  |
| V H50 B |  |  |  |  |
| V H50 C |  |  |  |  |

Note: Please refer to specific sections of the PQ-SPEC-01 for detailed compliance limits

95th Percentile VTHD and Individual Harmonic Spectrum Graph

[Insert 95th Percentile VTHD and Individual Harmonic Spectrum Graph here]

## Voltage Interharmonics Summary

The voltage interharmonics are represented as a percentage (%) of the fundamental (60Hz) voltage for each phase accordingly.

| IH Order | VaIH avg (%) | VaIH max (%) | VaIH C95 (%) | VbIH avg (%) | VbIH max (%) | VbIH C95 (%) | VcIH avg (%) | VcIH max (%) | VcIH C95 (%) |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| 1 |  |  |  |  |  |  |  |  |  |
| 2 |  |  |  |  |  |  |  |  |  |
| 3 |  |  |  |  |  |  |  |  |  |
| 4 |  |  |  |  |  |  |  |  |  |
| 5 |  |  |  |  |  |  |  |  |  |
| 6 |  |  |  |  |  |  |  |  |  |
| 7 |  |  |  |  |  |  |  |  |  |
| 8 |  |  |  |  |  |  |  |  |  |
| 9 |  |  |  |  |  |  |  |  |  |
| 10 |  |  |  |  |  |  |  |  |  |
| 11 |  |  |  |  |  |  |  |  |  |
| 12 |  |  |  |  |  |  |  |  |  |
| 13 |  |  |  |  |  |  |  |  |  |
| 14 |  |  |  |  |  |  |  |  |  |
| 15 |  |  |  |  |  |  |  |  |  |
| 16 |  |  |  |  |  |  |  |  |  |
| 17 |  |  |  |  |  |  |  |  |  |
| 18 |  |  |  |  |  |  |  |  |  |
| 19 |  |  |  |  |  |  |  |  |  |
| 20 |  |  |  |  |  |  |  |  |  |
| 21 |  |  |  |  |  |  |  |  |  |
| 22 |  |  |  |  |  |  |  |  |  |
| 23 |  |  |  |  |  |  |  |  |  |
| 24 |  |  |  |  |  |  |  |  |  |
| 25 |  |  |  |  |  |  |  |  |  |
| 26 |  |  |  |  |  |  |  |  |  |
| 27 |  |  |  |  |  |  |  |  |  |
| 28 |  |  |  |  |  |  |  |  |  |
| 29 |  |  |  |  |  |  |  |  |  |
| 30 |  |  |  |  |  |  |  |  |  |
| 31 |  |  |  |  |  |  |  |  |  |
| 32 |  |  |  |  |  |  |  |  |  |
| 33 |  |  |  |  |  |  |  |  |  |
| 34 |  |  |  |  |  |  |  |  |  |
| 35 |  |  |  |  |  |  |  |  |  |
| 36 |  |  |  |  |  |  |  |  |  |
| 37 |  |  |  |  |  |  |  |  |  |
| 38 |  |  |  |  |  |  |  |  |  |
| 39 |  |  |  |  |  |  |  |  |  |
| 40 |  |  |  |  |  |  |  |  |  |
| 41 |  |  |  |  |  |  |  |  |  |
| 42 |  |  |  |  |  |  |  |  |  |
| 43 |  |  |  |  |  |  |  |  |  |
| 44 |  |  |  |  |  |  |  |  |  |
| 45 |  |  |  |  |  |  |  |  |  |
| 46 |  |  |  |  |  |  |  |  |  |
| 47 |  |  |  |  |  |  |  |  |  |
| 48 |  |  |  |  |  |  |  |  |  |
| 49 |  |  |  |  |  |  |  |  |  |
| 50 |  |  |  |  |  |  |  |  |  |

95th Percentile Individual Voltage Interharmonic Spectrum Graph

[Insert 95th Percentile Individual Voltage Interharmonic Spectrum Graph here]

## Current TDD and Individual Current Harmonics Summary

Note: Compliant column is required for the compliance report but not required for benchmark report.

The current distortion and harmonics are based on CSA 22.3 No.9-08 standard.

| I Harmonic | Average (%) | Maximum (%) | CP 95 (%) | Limit (%) | Compliant (Yes/No) |
| --- | --- | --- | --- | --- | --- |
| I TDD A |  |  |  | 5 |  |
| I TDD B |  |  |  | 5 |  |
| I TDD C |  |  |  | 5 |  |
| I H2 A |  |  |  | 1 |  |
| I H2 B |  |  |  | 1 |  |
| I H2 C |  |  |  | 1 |  |
| I H3 A |  |  |  | 4 |  |
| I H3 B |  |  |  | 4 |  |
| I H3 C |  |  |  | 4 |  |
| I H4 A |  |  |  | 1 |  |
| I H4 B |  |  |  | 1 |  |
| I H4 C |  |  |  | 1 |  |
| I H5 A |  |  |  | 4 |  |
| I H5 B |  |  |  | 4 |  |
| I H5 C |  |  |  | 4 |  |
| I H6 A |  |  |  | 1 |  |
| I H6 B |  |  |  | 1 |  |
| I H6 C |  |  |  | 1 |  |
| I H7 A |  |  |  | 4 |  |
| I H7 B |  |  |  | 4 |  |
| I H7 C |  |  |  | 4 |  |
| I H8 A |  |  |  | 1 |  |
| I H8 B |  |  |  | 1 |  |
| I H8 C |  |  |  | 1 |  |
| I H9 A |  |  |  | 4 |  |
| I H9 B |  |  |  | 4 |  |
| I H9 C |  |  |  | 4 |  |
| I H10 A |  |  |  | 1 |  |
| I H10 B |  |  |  | 1 |  |
| I H10 C |  |  |  | 1 |  |
| I H11 A |  |  |  | 2 |  |
| I H11 B |  |  |  | 2 |  |
| I H11 C |  |  |  | 2 |  |
| I H12 A |  |  |  | 0.5 |  |
| I H12 B |  |  |  | 0.5 |  |
| I H12 C |  |  |  | 0.5 |  |
| I H13 A |  |  |  | 2 |  |
| I H13 B |  |  |  | 2 |  |
| I H13 C |  |  |  | 2 |  |
| I H14 A |  |  |  | 0.5 |  |
| I H14 B |  |  |  | 0.5 |  |
| I H14 C |  |  |  | 0.5 |  |
| I H15 A |  |  |  | 2 |  |
| I H15 B |  |  |  | 2 |  |
| I H15 C |  |  |  | 2 |  |
| I H16 A |  |  |  | 0.5 |  |
| I H16 B |  |  |  | 0.5 |  |
| I H16 C |  |  |  | 0.5 |  |
| I H17 A |  |  |  | 1.5 |  |
| I H17 B |  |  |  | 1.5 |  |
| I H17 C |  |  |  | 1.5 |  |
| I H18 A |  |  |  | 0.375 |  |
| I H18 B |  |  |  | 0.375 |  |
| I H18 C |  |  |  | 0.375 |  |
| I H19 A |  |  |  | 1.5 |  |
| I H19 B |  |  |  | 1.5 |  |
| I H19 C |  |  |  | 1.5 |  |
| I H20 A |  |  |  | 0.375 |  |
| I H20 B |  |  |  | 0.375 |  |
| I H20 C |  |  |  | 0.375 |  |
| I H21 A |  |  |  | 1.5 |  |
| I H21 B |  |  |  | 1.5 |  |
| I H21 C |  |  |  | 1.5 |  |
| I H22 A |  |  |  | 0.375 |  |
| I H22 B |  |  |  | 0.375 |  |
| I H22 C |  |  |  | 0.375 |  |
| I H23 A |  |  |  | 0.6 |  |
| I H23 B |  |  |  | 0.6 |  |
| I H23 C |  |  |  | 0.6 |  |
| I H24 A |  |  |  | 0.15 |  |
| I H24 B |  |  |  | 0.15 |  |
| I H24 C |  |  |  | 0.15 |  |
| I H25 A |  |  |  | 0.6 |  |
| I H25 B |  |  |  | 0.6 |  |
| I H25 C |  |  |  | 0.6 |  |
| I H26 A |  |  |  | 0.15 |  |
| I H26 B |  |  |  | 0.15 |  |
| I H26 C |  |  |  | 0.15 |  |
| I H27 A |  |  |  | 0.6 |  |
| I H27 B |  |  |  | 0.6 |  |
| I H27 C |  |  |  | 0.6 |  |
| I H28 A |  |  |  | 0.15 |  |
| I H28 B |  |  |  | 0.15 |  |
| I H28 C |  |  |  | 0.15 |  |
| I H29 A |  |  |  | 0.6 |  |
| I H29 B |  |  |  | 0.6 |  |
| I H29 C |  |  |  | 0.6 |  |
| I H30 A |  |  |  | 0.15 |  |
| I H30 B |  |  |  | 0.15 |  |
| I H30 C |  |  |  | 0.15 |  |
| I H31 A |  |  |  | 0.6 |  |
| I H31 B |  |  |  | 0.6 |  |
| I H31 C |  |  |  | 0.6 |  |
| I H32 A |  |  |  | 0.15 |  |
| I H32 B |  |  |  | 0.15 |  |
| I H32 C |  |  |  | 0.15 |  |
| I H33 A |  |  |  | 0.6 |  |
| I H33 B |  |  |  | 0.6 |  |
| I H33 C |  |  |  | 0.6 |  |
| I H34 A |  |  |  | 0.15 |  |
| I H34 B |  |  |  | 0.15 |  |
| I H34 C |  |  |  | 0.15 |  |
| I H35 A |  |  |  | 0.3 |  |
| I H35 B |  |  |  | 0.3 |  |
| I H35 C |  |  |  | 0.3 |  |
| I H36 A |  |  |  | 0.075 |  |
| I H36 B |  |  |  | 0.075 |  |
| I H36 C |  |  |  | 0.075 |  |
| I H37 A |  |  |  | 0.3 |  |
| I H37 B |  |  |  | 0.3 |  |
| I H37 C |  |  |  | 0.3 |  |
| I H38 A |  |  |  | 0.075 |  |
| I H38 B |  |  |  | 0.075 |  |
| I H38 C |  |  |  | 0.075 |  |
| I H39 A |  |  |  | 0.3 |  |
| I H39 B |  |  |  | 0.3 |  |
| I H39 C |  |  |  | 0.3 |  |
| I H40 A |  |  |  | 0.075 |  |
| I H40 B |  |  |  | 0.075 |  |
| I H40 C |  |  |  | 0.075 |  |
| I H41 A |  |  |  | 0.3 |  |
| I H41 B |  |  |  | 0.3 |  |
| I H41 C |  |  |  | 0.3 |  |
| I H42 A |  |  |  | 0.075 |  |
| I H42 B |  |  |  | 0.075 |  |
| I H42 C |  |  |  | 0.075 |  |
| I H43 A |  |  |  | 0.3 |  |
| I H43 B |  |  |  | 0.3 |  |
| I H43 C |  |  |  | 0.3 |  |
| I H44 A |  |  |  | 0.075 |  |
| I H44 B |  |  |  | 0.075 |  |
| I H44 C |  |  |  | 0.075 |  |
| I H45 A |  |  |  | 0.3 |  |
| I H45 B |  |  |  | 0.3 |  |
| I H45 C |  |  |  | 0.3 |  |
| I H46 A |  |  |  | 0.075 |  |
| I H46 B |  |  |  | 0.075 |  |
| I H46 C |  |  |  | 0.075 |  |
| I H47 A |  |  |  | 0.3 |  |
| I H47 B |  |  |  | 0.3 |  |
| I H47 C |  |  |  | 0.3 |  |
| I H48 A |  |  |  | 0.075 |  |
| I H48 B |  |  |  | 0.075 |  |
| I H48 C |  |  |  | 0.075 |  |
| I H49 A |  |  |  | 0.3 |  |
| I H49 B |  |  |  | 0.3 |  |
| I H49 C |  |  |  | 0.3 |  |
| I H50 A |  |  |  | 0.075 |  |
| I H50 B |  |  |  | 0.075 |  |
| I H50 C |  |  |  | 0.075 |  |

Note: Please refer to specific sections of the PQ-SPEC-01 for detailed compliance limits

95th Percentile ITHD and Individual Harmonic Spectrum Graph

[Insert 95th Percentile ITHD and Individual Harmonic Spectrum Graph here]

## Current Interharmonics Summary

All current interharmonics are a percentage of the rated current or 95 percentiles of the current during the monitoring period.

| IH order | IaIH avg (%) | IaIH max (%) | IaIH C95 (%) | IbIH avg (%) | IbIH max (%) | IbIH C95 (%) | IcIH avg (%) | IcIH max (%) | IcIH C95 (%) |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| 1 |  |  |  |  |  |  |  |  |  |
| 2 |  |  |  |  |  |  |  |  |  |
| 3 |  |  |  |  |  |  |  |  |  |
| 4 |  |  |  |  |  |  |  |  |  |
| 5 |  |  |  |  |  |  |  |  |  |
| 6 |  |  |  |  |  |  |  |  |  |
| 7 |  |  |  |  |  |  |  |  |  |
| 8 |  |  |  |  |  |  |  |  |  |
| 9 |  |  |  |  |  |  |  |  |  |
| 10 |  |  |  |  |  |  |  |  |  |
| 11 |  |  |  |  |  |  |  |  |  |
| 12 |  |  |  |  |  |  |  |  |  |
| 13 |  |  |  |  |  |  |  |  |  |
| 14 |  |  |  |  |  |  |  |  |  |
| 15 |  |  |  |  |  |  |  |  |  |
| 16 |  |  |  |  |  |  |  |  |  |
| 17 |  |  |  |  |  |  |  |  |  |
| 18 |  |  |  |  |  |  |  |  |  |
| 19 |  |  |  |  |  |  |  |  |  |
| 20 |  |  |  |  |  |  |  |  |  |
| 21 |  |  |  |  |  |  |  |  |  |
| 22 |  |  |  |  |  |  |  |  |  |
| 23 |  |  |  |  |  |  |  |  |  |
| 24 |  |  |  |  |  |  |  |  |  |
| 25 |  |  |  |  |  |  |  |  |  |
| 26 |  |  |  |  |  |  |  |  |  |
| 27 |  |  |  |  |  |  |  |  |  |
| 28 |  |  |  |  |  |  |  |  |  |
| 29 |  |  |  |  |  |  |  |  |  |
| 30 |  |  |  |  |  |  |  |  |  |
| 31 |  |  |  |  |  |  |  |  |  |
| 32 |  |  |  |  |  |  |  |  |  |
| 33 |  |  |  |  |  |  |  |  |  |
| 34 |  |  |  |  |  |  |  |  |  |
| 35 |  |  |  |  |  |  |  |  |  |
| 36 |  |  |  |  |  |  |  |  |  |
| 37 |  |  |  |  |  |  |  |  |  |
| 38 |  |  |  |  |  |  |  |  |  |
| 39 |  |  |  |  |  |  |  |  |  |
| 40 |  |  |  |  |  |  |  |  |  |
| 41 |  |  |  |  |  |  |  |  |  |
| 42 |  |  |  |  |  |  |  |  |  |
| 43 |  |  |  |  |  |  |  |  |  |
| 44 |  |  |  |  |  |  |  |  |  |
| 45 |  |  |  |  |  |  |  |  |  |
| 46 |  |  |  |  |  |  |  |  |  |
| 47 |  |  |  |  |  |  |  |  |  |
| 48 |  |  |  |  |  |  |  |  |  |
| 49 |  |  |  |  |  |  |  |  |  |

95th Percentile Individual Current Interharmonic Spectrum Graph

[Insert 95th Percentile Individual Current Interharmonic Spectrum Graph here]

## Voltage Flicker (Pst, Plt)

Pst/Plt Graph

[Insert Pst/Plt Graph here]

The 95th percentile value of Pst is Value.

The 95th percentile value of Plt is Value.

Note: The 95th percentile values of Pst and Plt should be below the standard limit of PQ-SPEC-01.

## RVC (Rapid Voltage Change)

Refer to 61000-4-30 Class A latest revision for detection and measurement method of RVC event.

Single transformer energization

Voltage RMS Graph

[Insert Voltage Graph here]

Current RMS Graph

[Insert Current Graph here]

The RVC of single transformer energization (size of transformer) results in (value)%.

All transformer energization (If no other switchgears that can automatically do a group of transformer energization)

Voltage RMS Graph

[Insert Voltage Graph here]

Current RMS Graph

[Insert Current Graph here]

The RVC of all transformer energization (number of transformer x single transformer size) simultaneously results in (value)%.

Note: If energizing all transformers is not realistic because the facility have switchgear switches that either switch each transformers at a time, or switches a portion of the total transformers at a time, then state the switching philosophy clearly and why capture is obtained for the specific worst case switching scenario.

## Power and Power Factor

Power and Power Factor Graph

[Insert Power and Power Factor Graph here]

The real power on each phase varies between range of real power (e.g. kW (load) and -kW (generation)) during the monitoring period, with power factor varying between range of power factor.

Note: The Power Factor setting should be the same as the agreed operating power factor during generation periods.

# Summary of the Measurement Results

The summary of power quality compliance assessments are shown below assessment period between Year-Month-Date and Year-Month-Date.

Note: Summary of the assessment is required for the compliance report but not required for benchmark report.

Detailed data and charts are presented in following sections for PQ indices that are identified to be not in compliance with the specification.

| Assessments | Compliant (Yes/No) |
| --- | --- |
| Voltage THD and Individual Harmonics |  |
| Current TDD and Individual Harmonics |  |
| Voltage Flicker (Pst and Plt) |  |
| RVC |  |

Note: Please refer to specific sections of the PQ-SPEC-01 for detailed compliance limits

## Additional Comments

| ## Provided by: |  |
| --- | --- |
| Power Producer or Engineering Consultant (name / company) |  |
| Title (P.Eng Required) |  |
| Signature |  |
| Date |  |

Power Quality report to be reviewed by engineering, customer/consultant shall be contacted directly if any questions regarding the content.